## Single Point Load Data
Dakota Smart-Strut Single Point Load Data
[7 empty] | FIXED BEAM SUPPORT OPEN END UP |  |  | SUSPENDED SIMPLE BEAM SUPPORT OPEN END DOWN
Part # | Length | Gauge | Height | 9/16” x 1-1/8” Horizontal Slots | .118” x .787” Vertical Slots | Bolted Mounting Span (in) (MAX Suspension Point) Tesing Mounting Torque - 300 in/lb | Test Fixture Inside Span (in) | Max* Load (lb) | Deflection at Max Load (in) | Max* Load (lb) | Deflection at Max Load (in)
DS-SS15812-14-PG | 1’ 2” (14”) | 12 GA | 1-5/8” | 2 | 32 | 12" | 10 | 2120 | 0.013 | 1350 | 0.038
DS-SS15812-18-PG | 1’ 6” (18”) |  |  | 2 | 44 | 16" | 14 | 1625 | 0.02 | 1200 | 0.054
DS-SS15812-24-PG | 2’ 0” (24”) |  |  | 2 | 64 | 22" | 20 | 1300 | 0.04 | 1065 | 0.087
DS-SS15812-30-PG | 2’ 6” (30”) |  |  | 4 | 64 | 28" | 26 | 900 | 0.052 | 750 | 0.106
DS-SS15812-42-PG | 3’ 6” (42”) |  |  | 6 | 96 | 40" | 38 | 650 | 0.096 | 490 | .167 (Span/240)
DS-SS15812-54-PG | 4’ 6” (54”) |  |  | 12 | 96 | 52" | 50 | 450 | 0.137 | 380 | .279 (Span/240 +1/16)
DS-SS15812-66-PG | 5’ 6” (66”) |  |  | 12 | 128 | 64" | 62 | 425 | 0.232 | 248 | .329 (Span/240 +1/16)
DS-SS15812-78-PG | 6’ 6” (78”) |  |  | 14 | 160 | 76" | 74 | 394 | .379 (Span/240 + 1/16) | 172 | .379 (Span/240 +1/16)
DS-SS15812-90-PG | 7’ 6” (90”) |  |  | 14 | 192 | 88" | 86 | 320 | .429 (Span/240 + 1/16) | 135 | .429 (Span/240 +1/16)
DS-SS15812-102-PG | 8’6” (102”) |  |  | 14 | 224 | 100" | 98 | 267 | .479 (Span/240 + 1/16) | 98 | .479 (Span/240 +1/16)
*Load is determined using a 3X Safety Factor
[7 empty] | FIXED BEAM SUPPORT OPEN END UP |  |  | SUSPENDED SIMPLE BEAM SUPPORT OPEN END DOWN
Part # | Length | Gauge | Height | 9/16” x 1-1/8” Horizontal Slots | .118” x .787” Vertical Slots | Bolted Mounting Span (in) (MAX Suspension Point) Tesing Mounting Torque - 300 in/lb | Test Fixture Inside Span (in) | Max* Load (lb) | Deflection at Max Load (in) | Max* Load (lb) | Deflection at Max Load (in)
DS-SS131612-14-PG | 1’ 2” (14”) | 12 GA. | 13/16” | 2 | 32 | 12" | 10 | 1030 | 0.022 | 650 | 0.05
DS-SS131612-18-PG | 1’ 6” (18”) |  |  | 2 | 44 | 16" | 14 | 700 | 0.033 | 460 | 0.068
DS-SS131612-24-PG | 2’ 0” (24”) |  |  | 2 | 64 | 22" | 20 | 495 | 0.053 | 275 | 0.107
DS-SS131612-30-PG | 2’ 6” (30”) |  |  | 4 | 64 | 28" | 26 | 365 | 0.076 | 195 | .148 (Span/240 +1/32)
DS-SS131612-42-PG | 3’ 6” (42”) |  |  | 6 | 96 | 40" | 38 | 250 | 0.145 | 109 | .229 (Span/240 +1/16)
DS-SS131612-54-PG | 4’ 6” (54”) |  |  | 12 | 96 | 52" | 50 | 197 | .279 (Span/240 + 1/32) | 61 | .279 (Span/240 +1/16)
DS-SS131612-66-PG | 5’ 6” (66”) |  |  | 12 | 128 | 64" | 62 | 147 | .329 (Span/240 + 1/16) | N/A
DS-SS131612-78-PG | 6’ 6” (78”) |  |  | 14 | 160 | 76" | 74 | 105 | .379 (Span/240 + 1/16) | N/A
*Load is determined using a 3X Safety Factor

## Distributed Load Data
Dakota Smart-Strut Distributed Load Data
[6 empty] | FIXED BEAM SUPPORT 2 Equal CONCENTRATED LOADS AT 1/4 pts UDL LOAD DATA (2 PIPES ON TOP OF STRUT, OPEN END UP) |  |  |  |  | SUSPENDED SIMPLE BEAM SUPPORT 2 Equal CONCENTRATED LOADS AT 1/4 pts UDL LOAD DATA (2 PIPES ON TOP OF STRUT, OPEN END DOWN)
Part # | Length | Gauge | Height | 9/16” x 1-1/8” Horizontal Slots | .118” x .787” Vertical Slots | Bolted Mounting Span (in) (MAX Suspension Point) Testing Mounting Torque - 300 in/lb | Test Fixture Inside Span (in) | 1/4 Span Distance (in) | Max* Load (lb) | Deflection at Max Load (in) | Suspended Span (in) | 1/4 Span Distance (in) | Max* Load (lb) | Deflection at Max Load (in)
DS-SS15812-14-PG | 1’ 2” (14”) | 12 GA | 1-5/8” | 2 | 32 | 12 | 10 | 3.165 | 2800 | 0.015 | 12 | 3.165 | 2000 | 0.046
DS-SS15812-18-PG | 1’ 6” (18”) |  |  | 2 | 44 | 16 | 14 | 3.905 | 2700 | 0.026 | 16 | 3.905 | 1700 | 0.057
DS-SS15812-24-PG | 2’ 0” (24”) |  |  | 2 | 64 | 22 | 20 | 5.645 | 1675 | 0.035 | 22 | 5.645 | 1550 | 0.089
DS-SS15812-30-PG | 2’ 6” (30”) |  |  | 4 | 64 | 28 | 26 | 7.07 | 1455 | 0.05 | 28 | 7.07 | 1335 | 0.13
DS-SS15812-42-PG | 3’ 6” (42”) |  |  | 6 | 96 | 40 | 38 | 9.92 | 1150 | 0.124 | 40 | 9.92 | 835 | 0.198
DS-SS15812-54-PG | 4’ 6” (54”) |  |  | 12 | 96 | 52 | 50 | 13.085 | 850 | 0.174 | 52 | 13.085 | 575 | 0.279
DS-SS15812-66-PG | 5’ 6” (66”) |  |  | 12 | 128 | 64 | 62 | 15.935 | 600 | 0.21 | 64 | 15.935 | 370 | 0.329
DS-SS15812-78-PG | 6’ 6” (78”) |  |  | 14 | 160 | 76 | 74 | 19.1 | 550 | 0.348 | 76 | 19.1 | 264 | 0.379
DS-SS15812-90-PG | 7’ 6” (90”) |  |  | 14 | 192 | 88 | 86 | 21.95 | 500 | 0.398 | 88 | 21.95 | 204 | 0.429
DS-SS15812-102-PG | 8’6” (102”) |  |  | 14 | 224 | 100 | 98 | 25.115 | 415 | 0.479 | 100 | 25.115 | 143 | 0.479
*Load is determined using a 3X Safety Factor
[6 empty] | FIXED BEAM SUPPORT 2 Equal CONCENTRATED LOADS AT 1/4 pts UDL LOAD DATA (2 PIPES ON TOP OF STRUT, OPEN END UP) |  |  |  |  | SUSPENDED SIMPLE BEAM SUPPORT 2 Equal CONCENTRATED LOADS AT 1/4 pts UDL LOAD DATA (2 PIPES ON TOP OF STRUT, OPEN END DOWN)
Part # | Length | Gauge | Height | 9/16” x 1-1/8” Horizontal Slots | .118” x .787” Vertical Slots | Bolted Mounting Span (in) (MAX Suspension Point) Tesing Mounting Torque - 300 in/lb | Test Fixture Inside Span (in) | 1/4 Span Distance (in) | Max* Load (lb) | Deflection at Max Load (in) | Suspended Span (in) | 1/4 Span Distance (in) | Max* Load (lb) | Deflection at Max Load (in)
DS-SS131612-14-PG | 1’ 2” (14”) | 12 GA. | 13/16” | 2 | 32 | 12" | 10 | 3.165 | 1600 | 0.017 | 12 | 3.165 | 1125 | 0.073
DS-SS131612-18-PG | 1’ 6” (18”) |  |  | 2 | 44 | 16" | 14 | 3.905 | 1100 | 0.029 | 16 | 3.905 | 970 | 0.098
DS-SS131612-24-PG | 2’ 0” (24”) |  |  | 2 | 64 | 22" | 20 | 5.645 | 850 | 0.042 | 22 | 5.645 | 575 | 0.154
DS-SS131612-30-PG | 2’ 6” (30”) |  |  | 4 | 64 | 28" | 26 | 7.07 | 700 | 0.079 | 28 | 7.07 | 350 | 0.179
DS-SS131612-42-PG | 3’ 6” (42”) |  |  | 6 | 96 | 40" | 38 | 9.92 | 550 | .167 Span/240 | 40 | 9.92 | 160 | 0.229
DS-SS131612-54-PG | 4’ 6” (54”) |  |  | 12 | 96 | 52" | 50 | 13.085 | 430 | .279 (Span/240 + 1/16) | 52 | 13.085 | 90 | 0.279
DS-SS131612-66-PG | 5’ 6” (66”) |  |  | 12 | 128 | 64" | 62 | 15.935 | 289 | .329 (Span/240 + 1/16) | 64 | 15.935 | 64 | 0.329
DS-SS131612-78-PG | 6’ 6” (78”) |  |  | 14 | 160 | 76" | 74 | 19.1 | 199 | .379 (Span/240 + 1/16) | 76 | 19.1 | N/A
*Load is determined using a 3X Safety Factor